## Overview
IDAP Energy Report Calculator
V1.0
2019-05-27
The intent of this workbook is to provide a platform in which to use the same ASHRAE 90.1 - 2016 Appendix G Baseline Model along with Performance Models to calculate metrics for IDAP, LEED V4 and/or City of Fort Collins Building Energy Code.
Use the IDAP Tab for calculating report values for the IDAP SD, DD and CD reports.
Use the LEED Tab for calculating Optimize Energy Performance credits for LEED V4 using ASHRAE 90.1 - 2016 Appendix G methodology.
Use the Code Tab to document compliance with City of Fort Collins Energy Code using the Performance Rating Method.
Provide any explanatory notes on the Notes worksheet.
For more detail, refer to the IDAP Program Manual, available at www.fcgov.com/idap .
Please report any issues with the spreadsheet to:
Gary Schroeder
Fort Collins Utilities
gschroeder@fcgov.com
970-221-6395

## IDAP
IDAP Calculations
Project Name
Date |  |  |  | = inputs
BPFs by space type(s) and area(s)
Space type | Area | BPFCode | BPFIDAP |  | ASHRAE 90.1 - 2016 Building Performance Factors
|  | 0 | 0 |  | For buildings permitted under IECC 2018
|  | 0 | 0 |  | Builiding Area Type | BPFCode | BPFIDAP
|  | 0 | 0 |  | Multifamily | 0.8 | 0.72
|  | 0 | 0 |  | Hotel/motel | 0.61 | 0.55
Total/Avg | 0 | 0 | 0 |  | Office | 0.61 | 0.55
[5 empty] | Restaurant | 0.58 | 0.52
Design Incentive | 5000 |  |  |  | Retail | 0.59 | 0.53
[5 empty] | School | 0.5 | 0.45
BBUEC |  | /yr (from 90.1-2016 App. G Model) |  |  | Warehouse | 0.61 | 0.55
BBREC |  | /yr (from 90.1-2016 App. G Model) |  |  | All others | 0.57 | 0.51
BBRECCode | 0 | /yr
BBPCode = | 0 | /yr
PBPt = | 0 | /yr
Design Package | PBPm | Savings | PBREC | % PBREC below code | PBPm Check* | Construction Incentive** | Peformance Incentive**
A
B
C
D
E
*Should match Column B (PBPm)
** Estimated
Code Baseline electricity and natural gas calculation to be used in Table 6 of DD and Final Energy Reports
Eu |  | kWh/yr
Er |  | kWh/yr
Ecode |  | kWh/yr
NGu |  | therms/yr
NGr |  | therms/yr
NGCode |  | therms/yr
Annual electric and natural gas use for the code baseline is calculated as follows:
ECode = Eu + (BPFCode x Er)
ECode = Electricity use of code baseline building, kWh/yr
Eu = Unregulated electricity use of baseline model, kWh/yr
Er = Regulated electricity use of baseline model, kWh/yr
NGCode = NGu + (BPFCode x NGr)
NGCode = Natural gas use of code baseline building, therms/yr
NGu = Unregulated natural gas use of baseline model, therms/yr
NGr = Regulated natural gas use of baseline model, therms/yr
*Similar approach will be used for other fuels.

## LEED
LEED Optimize Energy Performance Calculations
Project Name
Date |  |  |  | = inputs
BPFs by space type(s) and area(s) - area weighted BPF |  |  |  |  | LEED Building Performance Factors (BPFs)* |  | Table 1. Points for percentage imporovement in energy performance*
LEED Space Type | Area | BPFLEED |  |  | LEED Alternative Performance Rating Method |  | New Construction | Major Renovation | Core and Shell | Points (except Schools, Healthcare) | Point Healthcare | Points Schools
|  | 0 |  |  | Rating System Adaptation | BPF | 6% | 4% | 3% | 1 | 3 | 1
|  | 0 |  |  | New Construction (Except High-Rise Residential) | 0.72 | 8% | 6% | 5% | 2 | 4 | 2
|  | 0 |  |  | Retail (Incl. Restaurant) | 0.72 | 10% | 8% | 7% | 3 | 5 | 3
Total/Avg | 0 | 0 |  |  | School | 0.65 | 12% | 10% | 9% | 4 | 6 | 4
[5 empty] | Healthcare | 0.69 | 14% | 12% | 11% | 5 | 7 | 5
[5 empty] | Hospitality | 0.76 | 16% | 14% | 13% | 6 | 8 | 6
BBUEC |  |  |  |  | Warehouse | 0.7 | 18% | 16% | 15% | 7 | 9 | 7
BBREC |  |  |  |  | Homes Mid-Rise & NC High-Rise Residential | 0.89 | 20% | 18% | 17% | 8 | 10 | 8
BBP (Baseline Building Performance) |  |  |  |  | *Standard 90.1-2010 |  | 22% | 20% | 19% | 9 | 11 | 9
PCIt* (Performance Cost Index Target) | [6 empty] | 24% | 22% | 21% | 10 | 12 | 10
*PCIt = [BBUEC + (BPFLEED x BBREC)]/BBP (ASHRAE 90.1 - 2016, 4.2.1.1) | [6 empty] | 26% | 24% | 23% | 11 | 13 | 11
[7 empty] | 29% | 27% | 26% | 12 | 14 | 12
Results | [6 empty] | 32% | 30% | 29% | 13 | 15 | 13
Design Package | PBP* | PCI** | % Improvement | LEED Points |  |  | 35% | 33% | 32% | 14 | 16 | 14
A | [6 empty] | 38% | 36% | 35% | 15 | 17 | 15
B | [6 empty] | 42% | 40% | 39% | 16 | 18 | 16
C | [6 empty] | 46% | 44% | 43% | 17 | 19 | -
D | [6 empty] | 50% | 48% | 47% | 18 | 20 | -
E | [6 empty] | *From LEED V4 for Building Design and Construction, January 11, 2019
*Proposed Building Performance = Unregulated and Regulated energy cost of proposed building
**Performance Cost Index = Proposed Building Performance/Baseline Building Performance (ASHRAE 90.1 - 2016, G1.2.2)

## Code
City of Fort Collins Code Calculations - ASHRAE Performance Rating Method
Project Name
Date
Address
Permit Number |  |  |  | = inputs
BPFs by space type(s) and area(s) - area weighted BPF |  |  |  |  | ASHRAE 90.1 - 2016 Building Performance Factors
Space Type | Area | BPFCode |  |  | For buildings permitted under IECC 2018
|  | 0 |  |  | Builiding Area Type | BPFCode
[5 empty] | Multifamily | 0.8
|  | 0 | 0 |  | Hotel/motel | 0.61
|  | 0 | 0 |  | Office | 0.61
Total/Avg | 0 | 0 |  |  | Restaurant | 0.58
[5 empty] | Retail | 0.59
Performance Cost Index Target |  |  |  |  | School | 0.5
BBUEC |  |  |  |  | Warehouse | 0.61
BBREC |  |  |  |  | All others | 0.57
BBP (Baseline Building Performance) | 0
PCIt*
*PCIt = [BBUEC + (BPFLEED x BBREC)]/BBP (ASHRAE 90.1 - 2016, 4.2.1.1)
Results
Design Package | PBP* | PCI** | Meets Code?
A
B
C
D
E
*Proposed Building Performance
**PCI=Proposed Building Performance/Baseline Building Performance